## Slide 1
MindSphere 3.0
MindConnect
Device Training

## Slide 2: MindConnect Device Training Learning Goals
MindConnect concept
Evaluate the connectivity requirements
Select the most suitable MindConnect option
Configure MindConnect elements in TIA-Portal using S7/ OPC UA protocols, OPC UA server and MindSphere
What are the MindConnect elements
&
how to get connected to MindSphere?
Notes: Go through the agenda of today’s training with explanation for each item
MSPH Ecosystem -> How does it look like & what parts do exist in the MSPH ecosystem?
MSPH Scalable Portfolio -> What does MSPH currently offer (e.g. infrastructure, APIs, apps)?
IT security -> How do we make sure your data is safe and no one has unauthorized access to your data?
Demonstration/Hands-On -> Probably most interesting part as we onboard a device to MSPH and let actually a training participant connect the device with MSPH
Use Cases - MindApps & Connectivity -> For which use cases can MindSphere be used or is being used already? What are the benefits for our customers?
MSPH Pricing Model -> Chapter to illustrate the costs which will be something most participants want to know
MSPH forums and networks -> How do I as a customer get in touch, e.g. to get help or answers to general questions?

## Slide 3
How to connect?

## Slide 4
MindSphere
Introduction

## Slide 5: MindSphere Introduction Learning Goals
Overview of MindSphere connect elements
The structure of the connectivity of MindSphere
How does the MindSphere ecosystem look like
&
What are the gateways of MindSphere?
Notes: Go through the agenda of today’s training with explanation for each item
MSPH Ecosystem -> How does it look like & what parts do exist in the MSPH ecosystem?
MSPH Scalable Portfolio -> What does MSPH currently offer (e.g. infrastructure, APIs, apps)?
IT security -> How do we make sure your data is safe and no one has unauthorized access to your data?
Demonstration/Hands-On -> Probably most interesting part as we onboard a device to MSPH and let actually a training participant connect the device with MSPH
Use Cases - MindApps & Connectivity -> For which use cases can MindSphere be used or is being used already? What are the benefits for our customers?
MSPH Pricing Model -> Chapter to illustrate the costs which will be something most participants want to know
MSPH forums and networks -> How do I as a customer get in touch, e.g. to get help or answers to general questions?

## Slide 6: MindSphere Portfolio Overview
MindSphere Applications
Powerful industry applications and digital services for asset transparency and analytical insights
MindSphere & MindAccess
Open Platform as a Service (PaaS) for scalable, global IoT connectivity and application development
Secure plug and play connection of Siemens and third-party products and equipment
MindConnect
MindServices
Training Consultancy Proof of Value Co-creation Support …
Notes: MindConnect - Secure plug and play connection of Siemens and third-party products
MindSphere Open Platform as a Service (PaaS) for scalable, global IoT connectivity and application development
MindApps - Powerful industry applications and digital services for asset transparency and analytical insights into products, plants, systems and machines – -------------Will MindApps be sold through the Industrial Mall?-----------

## Slide 7: MindSphere Portfolio Overview
MindSphere Applications
MindSphere & MindAccess
Open standards, including OPC UA
Plug and play
Secure and encrypted data communication
MindConnect
MindServices
Notes: First: How do I connect my assets?
Answer: MindConnect which offers you plug&play solutions with open standards including OPC UA and S7
- Secure connection and data communication of Siemens and third-party products

## Slide 8: MindSphere Overview

## Slide 9: MindSphere Connectivity

## Slide 10: Connectivity MindSphere MindConnect (3.0)
MindConnect
MindConnect Nano
MindConnect IoT2040 >> comes past o2/2018 <<
MindConnect Lib
MindConnect APIs
Already released
ü
With MindConnect provides multiple, varied and easy-to-implement connectivity solutions (connectors, agents, libraries, …) to be able to onboard a wide range of assets (Siemens and 3rd-party) in both brown- and greenfield environments as well as Siemens or 3rd-party systems.
For assets which can not be onboarded from scratch, the MindSphere also enables self programming of connectivity modules by using the APIs.
MindSphere Lib and APIs
MindSphere IoT Connectors
3rd Party Connectivity

## Slide 11: Connecting Assets to MindSphere (2.0)
MindConnect
MindConnect
Nano
MindConnect
IoT2040
MindConnect
FB 1500
MindConnect LIB
With MindConnect MindSphere provides multiple, varied and easy-to-implement connectivity solutions to onboard a wide range of assets (Siemens and 3rd-party) in both brown- and greenfield:
Focusing on brownfield installations, dedicated IoT Connectors like MindConnect Nano and MindConnect IoT2040, which provide plug and play connection of Siemens and 3rd party products thanks to communication via open standards like OPC UA
MindConnect embedded agents in Siemens industrial products like SIMATIC and SINUMERIK focusing on greenfield projects
For every further product, including 3rd-party, MindConnect LIB, which enables self programming of connectivity modules by interacting with the MindSphere southbound APIs
Software/ Embedded Solutions
Hardware Solutions

## Slide 12: MindSphere Connectivity Suite MindConnect Nano
MindConnect Nano is a device for collecting data using different protocols and transferring the data to MindSphere. The device supports transmission of data through a secure internet connection, to enable cloud-based applications and services.
  Fast and easy connectivity of industrial machines and automation systems to MindSphere
  Data collection via standard industrial protocols
  Software update management – Always up to date
  Rugged design for maintenance-free, continuous operation
  Comprehensive security concept in accordance with applicable industry standards
  Up to 500MB local data buffer
  Siemens S7 (for collecting data from S7-3xx / S7-4xx / ET-200s PLCs);
  OPC UA (for collecting data from all data sources which can provide data via an OPC UA server); the MindSphere Nano supports data collection with Part 8 of the OPC UA specification (Data Access)
  Additional Field protocols will follow
  Data reading cycle: Up to 250 data points / second
  Data transfer cycle: Every 10 seconds
Description
Benefits
Supporting Protocols
Performance
Hardware Gateway
1

## Slide 13: MindSphere Connectivity Suite MindConnect IoT2040
MindConnect IoT2040 is a device for collecting data using different protocols and transferring the data to MindSphere. The device supports transmission of data through a secure internet connection, to enable cloud-based applications and services.
  Fast and easy connectivity of industrial machines and automation systems to MindSphere
  Data collection via standard industrial protocols
  Software update management – Always up to date
  Rugged design for maintenance-free, continuous operation
  Comprehensive security concept in accordance with applicable industry standards
  Up to 500MB local data buffer
  Siemens S7 (for collecting data from S7-3xx / S7-4xx / ET-200s PLCs);
  OPC UA (for collecting data from all data sources which can provide data via an OPC UA server); the MindSphere Nano supports data collection with Part 8 of the OPC UA specification (Data Access)
  Additional Field protocols will follow
  Data reading cycle: Up to 30 data points / second
  Data transfer cycle: Every 10 seconds
Description
Benefits
Supporting Protocols
Performance
Hardware Gateway
1

## Slide 14: Structure of MindSphere Connectivity MindConnect Nano/ IoT2040
10
01
01
11
00
10
10
01
01
11
10
01
01
11
10
01
01
11
00
10
MindSphere
OR
S7
S7-1500 with OPC UA Server
OR OPC UA Server
MindConnect Nano
MindConnect IoT2040
With TIA Portal V14
10
01
01
11
10
01
01
11
00
10
Asset
Asset
MindConnect Elements
MindSphere
To use OPC UA together with MindSphere, you need a S7-1500 V2.x or an OPC UA server.
+
OR

## Slide 15: MindSphere Connectivity Suite MindConnect FB 1500*
MindConnect FB is a TIA Portal STEP7 Library to extend the functionality of the S7-1500 PLC. It supports encrypted transmission of PLC data to MindSphere through a secure internet connection, to enable cloud-based applications and services.
  Fast and easy connectivity of industrial machines and automation systems to MindSphere
  Simple configuration and commissioning - Configure your data model in STEP 7 (TIA Portal V14)
  No additional hardware needed
  Unencrypted onsite (local) traffic which allows local package inspection
  Comprehensive security concept in accordance with applicable industry standards
  Local data buffering possible
  S7-1500 acts as gateway into field-level which allows access to various data sources
  Data reading cycle: Up to 110 data points per second can be configured in TIA Portal (the exact amount of data points depends on each controller)
  Data transfer cycle: Every 10 seconds
Description
Benefits
Supporting Protocols
Performance
* Compatible with S7-1511 to S7-1518 with firmware 2.0 or higher
Integrated Gateway
2

## Slide 16: Structure of MindSphere Connectivity MindConnect FB 1500
With MindConnect FB, you need no extra Hardware Gateway to connect to MindSphere!
STEP7 TIA Portal V14
MindConnect FB
Asset
S7 1500
MindSphere

## Slide 17: MindSphere Connectivity Suite MindConnect LIB
  Enables connectivity for almost every asset (Siemens and 3rd party)
  Requires only a small number of system resources
  Secure connectivity from an onsite device to the MindSphere platform (e.g. authentication, encryption)
  Firewall-friendly communication via RESTfull API
  Logical workflows: Implement triggers to specify the calls that initiate a run of your data collection, integration and transfer processes
  File transfer functionality
  Local data buffering possible
Benefits
MindConnect LIB is a software development kit (SDK) which enables self programming of customer or use case specific connectivity agents by interacting with the MindSphere southbound APIs. It supports encrypted transmission of onsite data to MindSphere through a secure internet connection, to enable cloud-based applications and services
Description
  Data reading cycle: Depending on each use case, up to 250 data points per second for the first released version
  Data transfer cycle: Every 10 seconds
Performance
  Depends on your local decision as to where the MindConnect LIB is going to be used, including interface to custom data parser at the platform backend for non timeseries data. Generally speaking: Any field protocol could be supported (with development into the Custom Agent)
Supporting Protocols
Software Gateway
3

## Slide 18: Connectivity MindConnect IoT Extension (3.0)
MindConnect IoT Extension1) Expand MindSphere connectivity to all machines across the production floor
SW Agents: MQTT Agent, Java Agent, C++ Agent
Agent Development: REST API
Field protocols: HTTP/HTTPS, TCP, VNC, MQTT / MQTT+TLS, REST, SmartRest 1.0 / 2.0, OPC-UA, Modbus/RTU, Modbus/TCP, CAN bus, MMC, SPI, I2C, McASP, device specific protocols
Devices: Adeunis LoRAWAN, BeagleBone Black, Cinterion Java Modules, CloudGate, Dell Edge Gateway, INSYS Smart Devices – INSYS OS, INSYS Smart Devices – icom OS, Janz Tec emPC A/RPI, Libelium-Mesehlium, Mbed u-blox C027, Meitrack, Netcomm, PCUA Java Gateway, OWA3x, QuecLink, RaspberryPi, Red Lion RAM, SMARTBox, Robustel, SIGFOX, SMARTBox IO, SMARTBox Mini, TC3G, Telic, TinkerForge, Tixi
1) Limited to small files and time series values

## Slide 19: Connectivity MindConnect Integration (3.0)
MindConnect Integration1) Establish connectivity with existing databases and enterprise systems to open new avenues of analysis
Cloud connectors: FTP(S), SOAP, REST, OData 2.0, OData 4.0, Alfabet, Cumulocity, Apps, BigQuery, Calendar, Cloud Storage, Contacts, Drive, Cloud Pub/Sub, Sheets,S3, SNS, SQS, Apache Solr, AvaTax, Concur, Coupa, Magento, Marketo, Microsoft Dynamics, NetSuite, SAP cloud, SAP Hana Marketing Cloud, Salesforce, Salesforce CRM, ServiceNow, Slack, StrikeIron, SuccesFactors, SugarCRM, Zendesk
On premise connectors: Ariba, OnRamp, LotusNotes, OFTP, Oracle, PeopleSoft, Remedy, SAP, SAP XI, Siebel, AS/400, JavaBeans, JDBC, Apache HIVE, MongoDB, Cassandra, HDFS, Apache Impala, Apache WebSphereMQ, Tuxedo, MSMQ, Apache Kafka
1) Limited to small files and time series values

## Slide 20
Connecting Assets to MindSphere: MindConnect
MindConnect API/LIB
  For assets which can not be onboarded from scratch, the MindConnect API enables self programming of own connectivity agents and use further modules like Agent Management, Firmware Updates, etc. The MindConnect LIB provides an application example to facilitate the development of connectivity agents using the MindConnect API.
MindConnect Edge Analytics
  Collect data at higher sampling rates and utilizing X-Tools as a collector and pre-processor for high dynamic signals.
MindConnect IoT Extension
Extend the range of IoT devices that can easily be connected to MindSphere (e.g. Raspberry Pi, SIGFOX, Dell Edge GW) or use further adaptable software-agents (e.g. MQTT, Java, C++ agents) on your custom device.
MindConnect Integration
Integrate cloud-based (e.g. Salesforce.com and on-premise based enterprise and data (e.g. historian server or SCADA systems) systems to MindSphere and enrich your data model with an extensive range of additional context data.
MindConnect Nano and MindConnect IoT2040
  Establish a plug and play connection to MindSphere and collect and buffer data from multiple field devices using dedicated IoT connectors like the MindConnect Nano or the MindConnect IoT2040 (for an entry level).

## Slide 21: MindSphere Introduction Learning Goals
How does the MindSphere ecosystem look like?
Open and large; scaling fast; contains large and small partners of different sectors
What are the gateways of MindSphere?
Hardware Gateway with MindConnect Nano/ IoT2040, Integrated Gateway with S7 1500 or Software Gateway with MindConnect LIB

## Slide 22
MindSphere
Launchpad

## Slide 23: MindSphere Launchpad Learning Goals
Asset Manager
Fleet Manager
Application Manager
Manage MyMachines
How does the MindSphere Launchpad look like?
Notes: Go through the agenda of today’s training with explanation for each item
MSPH Ecosystem -> How does it look like & what parts do exist in the MSPH ecosystem?
MSPH Scalable Portfolio -> What does MSPH currently offer (e.g. infrastructure, APIs, apps)?
IT security -> How do we make sure your data is safe and no one has unauthorized access to your data?
Demonstration/Hands-On -> Probably most interesting part as we onboard a device to MSPH and let actually a training participant connect the device with MSPH
Use Cases - MindApps & Connectivity -> For which use cases can MindSphere be used or is being used already? What are the benefits for our customers?
MSPH Pricing Model -> Chapter to illustrate the costs which will be something most participants want to know
MSPH forums and networks -> How do I as a customer get in touch, e.g. to get help or answers to general questions?

## Slide 24: MindSphere Launchpad Overview (3.0)

## Slide 25
The Asset Manager offers the means to configure Assets, Asset type and Aspect type
Asset Manager

## Slide 26: MindSphere 3.0 Asset Manager
IoT Data Modeler is replaced by Asset Manager.
• Asset: assets can be created, onboarded, modified, cloned, moved, deleted or offboarded.
• Assets Types: administration of Assets Types/Templates.
• Aspect Types: administration of Aspect Types/Templates.

## Slide 27: MindSphere 3.0 Asset Manager
Assets Creates an asset in the three main topics: device types, agent types and hierarchy types. You can configure, read and manage an asset or the root asset. An asset is accessed by its ID.
Aspects You can manage all aspects of an asset. An aspect is the representation of the data sources of an agent. The measured time series data are stored for aspects. An aspect can contain multiple variables.

## Slide 28: MindSphere 3.0 Asset and Hierarchy
BasicAsset
BasicHierarchy
RootHierarchy
BasicArea
BasicSite
BasicEnterprise
MindConnect Nano
MindConnect IoT2040
MindConnect FB 1500
MindConnect Integration
MindConnect LIB
BasicDevice
BasicAgent

## Slide 29
Fleet
Management
Always up to date
The key data for your connected components and systems

## Slide 30: MindSphere 3.0 Fleet Manager
Transparency of
installed base
Analysis for each asset cluster of multiple data sources
Request function, defining actions after an occurrence of an event
Map View
    Equipment transparency:
    Live process data
    Root cause analysis
    Rule triggered events
Notes:   transparency of installed base
  An Asset is a logical representation of a machine or a system with one or multiple components
  For each asset cluster of multiple data sources which are required for a specific analysis Aspects (e.g., pressure, temperature, etc.) can be created
  A Map View shows the geographic location of connected Assets. Users see the recorded data in different diagrams. The user defines the data display timeframe
  The Request function helps users defining resulting actions after occurrence of an event, such as exceeding a limit

## Slide 31: Fleet Manager Visual Analyzer
    Visualize the data:
    Select visualization
    Select time frame
    Save and share current view
Notes:   transparency of installed base
  An Asset is a logical representation of a machine or a system with one or multiple components
  For each asset cluster of multiple data sources which are required for a specific analysis Aspects (e.g., pressure, temperature, etc.) can be created
  A Map View shows the geographic location of connected Assets. Users see the recorded data in different diagrams. The user defines the data display timeframe
  The Request function helps users defining resulting actions after occurrence of an event, such as exceeding a limit

## Slide 32: MindSphere Applications Hands-On Exercise 1
Hands-on
Exercise 1: MindSphere Launchpad and MindApp

## Slide 33: MindSphere Launchpad Summary
How does the MindSphere Launchpad look like?
Asset Manager, Fleet Manager, Visual Analyzer, Application Manager, UTS Reporting

## Slide 34
TIA Portal
Your gateway to automation in the Digital Enterprise

## Slide 35: TIA Portal Learning Goals
Unrestricted access to the complete range of digitalized automation
Integrates software and hardware
What is TIA Portal
&
why do we need it?
Notes: Go through the agenda of today’s training with explanation for each item
MSPH Ecosystem -> How does it look like & what parts do exist in the MSPH ecosystem?
MSPH Scalable Portfolio -> What does MSPH currently offer (e.g. infrastructure, APIs, apps)?
IT security -> How do we make sure your data is safe and no one has unauthorized access to your data?
Demonstration/Hands-On -> Probably most interesting part as we onboard a device to MSPH and let actually a training participant connect the device with MSPH
Use Cases - MindApps & Connectivity -> For which use cases can MindSphere be used or is being used already? What are the benefits for our customers?
MSPH Pricing Model -> Chapter to illustrate the costs which will be something most participants want to know
MSPH forums and networks -> How do I as a customer get in touch, e.g. to get help or answers to general questions?

## Slide 36: TIA Portal
TIA = Totally Integrated Automation
Supports process of product engineering and the connection of industrial software with automation- and production technology
It´s an automation development environment with “One Engineering Environment” approach
Engineering from one workplace and screen over whole supply chain
From planning to commissioning and maintenance
Increasing automation systems
Using the TIA portal, automation solutions in the production phase can be further optimized.
TIA-portal opens up the entire functionality of the S7-1500 controller
STEP7 Professional is the common tool for configuring the hardware set-up and the programming of the user program together with the program simulation and the diagnosis
TIA Portal is a tool to make all settings for your data points which should be collected from your asset and send to MindConnect Elements or MindSphere.

## Slide 37: TIA Portal Hands-On Exercise 2
Hands-on
Get 3 Data Points from S7-300 in TIA Portal for MindSphere

## Slide 38: TIA Portal Summary
What is TIA Portal and
why do we need it?
Unrestricted access to the complete range of digitalized automation
Integrates software and hardware

## Slide 39
MindSphere Assets
Configuration with S7
2018

## Slide 40: MindSphere Assets Learning Goals
Create an asset in MindSphere
Connect an asset in MindSphere via S7 protocol
Learn the onboarding process of MindConnect Nano
How do I create and connect an asset via S7 protocol in MindSphere?
Notes: Go through the agenda of today’s training with explanation for each item
MSPH Ecosystem -> How does it look like & what parts do exist in the MSPH ecosystem?
MSPH Scalable Portfolio -> What does MSPH currently offer (e.g. infrastructure, APIs, apps)?
IT security -> How do we make sure your data is safe and no one has unauthorized access to your data?
Demonstration/Hands-On -> Probably most interesting part as we onboard a device to MSPH and let actually a training participant connect the device with MSPH
Use Cases - MindApps & Connectivity -> For which use cases can MindSphere be used or is being used already? What are the benefits for our customers?
MSPH Pricing Model -> Chapter to illustrate the costs which will be something most participants want to know
MSPH forums and networks -> How do I as a customer get in touch, e.g. to get help or answers to general questions?

## Slide 41: Configuration with S7 Requirements for Configuration
MindConnect Nano/IoT 2040 is mounted on your asset
MindConnect Nano/IoT 2040 is prepared (refer to Getting Started MCN/IoT 2040 Chapter 3)
PC with internet access, USB stick (FAT or FAT32)
Valid credentials for MindSphere
You can find the Getting Started Guides on SIOS!

## Slide 42: Configuration with S7 What is S7 protocol
S7 protocol is Siemens’ standard protocol for industrial communication.
It is supported by all available S7 controllers and communication processors. Furthermore, PC systems with appropriate hardware and software support communication via the S7 protocol.
Features, e.g.:
Block orientated: it is divided in Protocol Data Units
Independent of the bus medium
Function oriented: each transmission contains a command or a reply
Structure:
In MindSphere, you can choose between S7 and OPC UA protocol!
Set of parameters
Parameters data
Data block
Header
Write this data into DB 10 starting from the offset 4.
Notes: S7comm (S7 Communication) is a Siemens proprietary protocol that runs between programmable logic controllers (PLCs) of the Siemens S7-300/400 family.
It is used for PLC programming, exchanging data between PLCs, accessing PLC data from SCADA (supervisory control and data acquisition) systems and diagnostic purposes

## Slide 43: Configuration with S7 S7 protocol

## Slide 44: Configuration with S7 Server and Client

## Slide 45: Configuration with S7 Hands-On Exercise 3
Hands-on
Onboarding of MindConnect Nano/IoT 2040 with MindSphere 3.0

## Slide 46: Configuration with S7 Hands-On Exercise 4
Hands-on
Configure data points with onboarded MindConnect Nano/IoT 2040

## Slide 47: Configuration with S7 Summary
What are the necessary steps to recieve data in MindSphere via MindConnect Nano and S7 protocol?
Create an Asset in MindSphere by choosing MindConnect Nano, fill in all relevant information and transfer configuration via USB stick to MindConnect Nano, create aspect and configure data points with S7 protocol

## Slide 48
MindSphere Assets
Configuration with OPC UA
2018

## Slide 49: Configuration with OPC UA Learning Goals
Connect an asset in MindSphere via OPC UA
What is OPC UA
and
How do I create and connect an asset via OPC UA in MindSphere?
Notes: Go through the agenda of today’s training with explanation for each item
MSPH Ecosystem -> How does it look like & what parts do exist in the MSPH ecosystem?
MSPH Scalable Portfolio -> What does MSPH currently offer (e.g. infrastructure, APIs, apps)?
IT security -> How do we make sure your data is safe and no one has unauthorized access to your data?
Demonstration/Hands-On -> Probably most interesting part as we onboard a device to MSPH and let actually a training participant connect the device with MSPH
Use Cases - MindApps & Connectivity -> For which use cases can MindSphere be used or is being used already? What are the benefits for our customers?
MSPH Pricing Model -> Chapter to illustrate the costs which will be something most participants want to know
MSPH forums and networks -> How do I as a customer get in touch, e.g. to get help or answers to general questions?

## Slide 50: Configuration with OPC UA What is OPC UA
OPC Unified Architecture (OPC UA) is an industrial M2M communication protocol for interoperability developed by the OPC Foundation.
It has a cross-platform service-oriented architecture for process control, while enhancing security and providing an information model for complex information structures.
Features, e.g.:
Discovery: find the available OPC Servers on local PCs and/or networks
Redundancy support
Heartbeat for connections in both directions (to indicate whether the other end is "alive").
With OPC UA, you are able to connect 3rd party assets to MindSphere!
To use OPC UA, you need an S7-1500 V2.x or any other OPC UA server!
Notes: Platform Independence:
Hardware platforms: traditional PC hardware, cloud-based servers, PLCs, micro-controllers (e.g. ARM)
Operating Systems: Microsoft Windows, Apple OSX, Android, or any distribution of Linux
Security:
Session Encryption - messages are transmitted securely at 128 or 256 bit encryption levels
Sequenced Packets - exposure to message replay attacks is eliminated with sequencing
Authentication - each UA client and server is identified through OpenSSL certificates providing control over which applications and systems are permitted to connect with each other
User Control - applications can require users to authenticate (login credentials, certificate, etc.) and can further restrict and enhance their capabilities with access rights and address-space “views”
Auditing - activities by user and/or system are logged providing an access audit trail

## Slide 51: Configuration with OPC UA Industry 4.0
Functional equivalence: all COM OPC Classic specifications are mapped to UA
  Discovery
  Address space
  On-demand
  Subscriptions
  Events
  Methods
Platform independence: from an embedded micro-controller to cloud-based infrastructure
Secure: encryption, authentication, and auditing
Extensible: ability to add new features without affecting existing applications
Comprehensive information modeling: for defining complex information
Notes: Discovery: find the availability of OPC Servers on local PCs and/or networks
Address space: all data is represented hierarchically (e.g. files and folders) allowing for simple and complex structures to be discovered and utilized by OPC Clients
On-demand: read and write data/information based on access-permissions
Subscriptions: monitor data/information and report-by-exception when values change based on a client’s criteria
Events: notify important information based on client’s criteria
Methods: clients can execute programs, etc. based on methods defined on the server

## Slide 52: Configuration with OPC UA Siemens Reference

## Slide 53: Configuration with OPC UA Information Modeling
The OPC UA information modeling framework turns data into information. With complete object-oriented capabilities, even the most complex multi-level structures can be modeled and extended.
➞ Transport – for the data exchange mechanisms between OPC UA applications. Different transport
protocols exist for different requirements (optimized for speed and throughput = UA TCP with UA Binary; firewall-friendly = HTTP + Soap).
➞ Meta model – specifies the rules and basic components for publishing an information model via OPC UA. It also includes various basic nodes and basic types.
➞ Services – they constitute the interface between a server as information provider and clients as users
of this information.
Notes: OPC UA was designed to support a wide range of
systems, ranging from PLC’s in production to enterprise
servers. These systems are characterized by
their diversity in terms of size, performance, platforms
and functional capabilities.
In order to meet these objectives, the following basic
functionalities were specifi ed for OPC UA:

## Slide 54: Configuration with OPC UA OPC UA Server and Client
Notes: http://documentation.unified-automation.com/uasdkcpp/1.2.0/L2OpcUaSoftwareLayers.html
OPC UA uses a similar client–server concept like Classic OPC. An application that wants to expose its own information to other applications is called UA server and an application that wants to consume information from other applications is called UA client. But it is expected that much more applications will be both UA server and UA client in one application than in Classic OPC. One reason is that more UA servers will be integrated directly in devices. Implementing also a UA client enables device to device communication. Another reason is the use of OPC UA as configuration interface, where UA clients are also UA servers to be configured via OPC UA.A typical OPC UA application is composed of three software layers shown in the following figure. The complete software stack can be implemented with C/C++, .NET, or JAVA. OPC UA is not limited to these programming languages and development platforms, but only these environments are currently used for implementing the OPC Foundation UA Stack deliverables.
An OPC UA Application is a system that wants to expose or to consume data via OPC UA. It contains the specific functionality for the application and the mapping of this functionality to OPC UA by using an OPC UA Stack and an OPC UA Software Development Kit (SDK).
An OPC UA client or server SDK implements common OPC UA functionality that is part of the application layer, since the UA Stacks implement only the communication channels. An OPC UA SDK reduces the development effort and facilitates faster interoperability for an OPC UA application.
An OPC UA Stack implements the different OPC UA transport mappings defined in UA Part 6. The Stack is used to invoke UA Services across process or network boundaries. OPC UA defines three Stack layers and different profiles for each layer. The message encoding layer defines the serialization of Service parameters in a binary and a XML format. The message security layer specifies how the messages must be secured by using the Web Service security standards or a UA binary version of the Web Service standards. The message transport layer defines the used network protocol, which could be UA TCP or HTTP and SOAP for Web Services. The following figure illustrates the different UA communication stack layers. The implementation of the layers in a UA Stack and the resulting API for the applications is not part of the OPC UA specification. The UA Stacks provide language-dependent APIs for UA client and UA server applications, but the Services and their parameters are similar and based on the abstract Service definition in UA Part 4.

## Slide 55: Configuration with OPC UA OPC UA Transport

## Slide 56: Configuration with OPC UA OPC UA Services
INTEGRATED SERVICES
OPC UA defines the services required to navigate through the namespace, read or write variables, or subscribing for data modifications and events. The OPC UA services are organized in logical groupings, so-called service sets. Service request and response are transmitted through exchange of messages between clients and servers.
➞ SecureChannel service set
➞ Session service set
➞ NodeManagement service set
➞ View service set
➞ Attribute service set
➞ Method service set
➞ MonitoredItem service set
➞ Subscription service set
Notes: https://opcfoundation.org/wp-content/uploads/2017/11/OPC-UA-Interoperability-For-Industrie4-and-IoT-EN.pdf
➞ SecureChannel service set This set includes services to determine the security configuration of a server and establish a communication channel in which the confidentiality and completeness (integrity) of the exchanged messages is guaranteed. These services are not implemented directly in the OPC UA application but are provided by the communication stack used.
➞ Session service set This service set defines services used to establish an application-layer connection (a session) on behalf of a specific user.
➞ NodeManagement service set These services provide an interface for the configuration of servers. It allows clients to add, modify, and delete nodes in the address space.
➞ View service set The view service set allows clients to discover nodes by browsing. Browsing allows clients to navigate up and down the hierarchy, or to follow references between nodes. This enables the client to explore the structure of the address space.
➞ Attribute service set The attribute service set is used to read and write attribute values. Attributes are primitive characteristics of nodes that are defined by OPC UA.
➞ Method service set Methods represent the function calls of objects. They are invoked and return after completion. The method service set defines the means to invoke methods.
➞ MonitoredItem service set This service can be used to determine which attributes from the address space should be monitored for changes by a client, or which events the client is interested in.
➞ Subscription service set Can be used to generate, modify or delete messages for MonitoredItems.

## Slide 57: Configuration with OPC UA Address Space Concepts
Notes: http://documentation.unified-automation.com/uasdkcpp/1.2.0/L2UaAddressSpaceConcepts.html
http://documentation.unified-automation.com/uasdkcpp/1.5.3/html/L2UaNodeClasses.html#L3UaNodeClassBase
INTEGRATED ADDRESS SPACE MODEL The object model enables production data, alarms, events and historic data to be integrated in a single OPC UA server. This allows, for example to represent a temperature measuring device as an object with its temperature value, alarm parameters and corresponding alarm limits. OPC UA integrates and standardizes the different address spaces and the services, so that OPC UA applications only require a single interface for navigation. The OPC UA address space is structured hierarchically, to foster the interoperability of clients and servers. The top levels are standardized for all servers. All nodes in the address space can be reached via the hierarchy. They can have additional references among each other, so that the address space forms a cohesive network of nodes. The OPC UA address space not only contains instances (instance space)
Description of OPC UA node classes.
Base Node Class
The base node class can not be used directly. It specifies the attributes available in all node classes.
The following attributes are available for each node class.
AttributeUseDataTypeDescriptionNodeIdMandatoryNodeIdUniquely identifies a Node in an OPC UA server and is used to address the Node in the OPC UA ServicesNodeClassMandatoryNodeClassAn enumeration identifying the NodeClass of a Node such as Object, Variable or MethodBrowseNameMandatoryQualifiedNameIdentifies the Node when browsing the OPC UA server. It is not localizedDisplayNameMandatoryLocalizedTextContains the Name of the Node that should be used to display the name in a user interface. Therefore, it is localizedDescriptionOptionalLocalizedTextThis optional Attribute contains a localized textual description of the NodeWriteMaskOptionalUInt32Is optional and specifies which Attributes of the Node are writable, i.e., can be modified by an OPC UA clientUserWriteMaskOptionalUInt32Is optional and specifies which Attributes of the Node can be modified by the user currently connected to the serverObject
The Object node class is used to represent systems, system components, real-world objects and software objects.
The following attribute is specific for the Object node class:
AttributeUseDataTypeDescriptionContains all attributes of the Base Node ClassEventNotifierMandatoryByteThis Attribute represents a bit mask that identifies whether the Object can be used to subscribe to Events and whether the history of Events is accessible and changeableVariable
The Variable node class is used to represent the content of an Object. Variables provide real data and thus the number of attributes is higher.
The following attributes are specific for the Variable node class:
AttributeUseDataTypeDescriptionContains all attributes of the Base Node ClassValueMandatoryBase Data TypeThe actual value of the Variable. The data type of the value is specified by the DataType, ValueRank, and ArrayDimensions AttributesDataTypeMandatoryNodeIdDataTypes are represented as Nodes in the Address Space. This Attribute contains a NodeId of such a Node and thus defines the DataType of the Value AttributeValueRankMandatoryInt32Identifies if the value is an array and when it is an array it allows specifying the dimensions of the arrayArrayDimensionsOptionalUInt32[]This optional Attribute allows specifying the size of an array and can only be used if the value is an array. For each dimension of the array a corresponding entry defines the length of the dimensionAccessLevelMandatoryByteA bit mask indicating whether the current value of the Value Attribute is readable and writable as well as whether the history of the value is readable and changeableUserAccessLevelMandatoryByteContains the same information as the AccessLevel but takes user access rights into accountMinimumSamplingIntervalOptionalDoubleThis optional Attribute provides the information how fast the OPC UA server can detect changes of the Value Attribute. For Values not directly managed by the server, e.g., the temperature of a temperature sensor, the server may need to scan the device for changes (polling) and thus is not able to detect changes faster than this minimum intervalHistorizingMandatoryBooleanIndicates whether the server currently collects history for the Value. The AccessLevel Attribute does not provide that information, it only specifies whether some history is availableMethod
The Method node class is used to represent a Method in the server address space.
The following attributes are specific for the Method node class.
AttributeUseDataTypeDescriptionContains all attributes of the Base Node ClassExecutableMandatoryBooleanA flag indicating if the Method can be invoked at the momentUserExecutableMandatoryBooleanSame as the Executable Attribute taking user access rights into accountReferenceType
The ReferenceType node class is used to represent the type of references used by the server.
The following attributes are specific for the ReferenceType node class:
AttributeUseDataTypeDescriptionContains all attributes of the Base Node ClassIsAbstractMandatoryBooleanSpecifies if the ReferenceType can be used for References or is only used for organizational purposes in the ReferenceType hierarchySymmetricMandatoryBooleanIndicates whether the Reference is symmetric, i.e., whether the meaning is the same in forward and inverse directionInverseNameOptionalLocalizedTextThis optional Attribute specifies the semantic of the Reference in inverse direction. It can only be applied for nonsymmetric References and must be provided if such a ReferenceType is not abstractObjectType
The ObjectType node class is used represents a type node for objects in the server address space. ObjectTypes are similar to a classes in object oriented languages.
The following attribute is specific for the ObjectType node class.
AttributeUseDataTypeDescriptionContains all attributes of the Base Node ClassIsAbstractMandatoryBooleanThis Attribute indicates whether the ObjectType is concrete or abstract and therefore cannot directly be used as type definitionVariableType
The VariableType node class is used represents a type node for variables in the server address space. VariableType are typically used to define which properties are available on the Variable instance.
The following attributes are specific for the VariableType node class:
AttributeUseDataTypeDescriptionContains all attributes of the Base Node ClassValueOptionalBase Data TypeThis optional Attribute defines a default value for instances of this VariableType. The data type of the value is specified by the DataType, ValueRank, and ArrayDimensions AttributesDataTypeMandatoryNodeIdDefines the DataType of the Value Attribute for instances of this type as well as for the Value Attribute of the VariableType if providedValueRankMandatoryInt32Identifies if the value is an array and when it is an array it allows specifying the dimensions of the arrayArrayDimensionsOptionalUInt32[]This optional Attribute allows specifying the size of an array and can only be used if the value is an array. For each dimension of the array a corresponding entry defines the length of the dimensionIsAbstractMandatoryBooleanThis Attribute indicates if the VariableType is abstract and therefore cannot directly be used as type definitionDataType
All DataTypes are represented as Nodes of the NodeClass DataType in the Address Space.
The following attribute is specific for the DataType node class:
AttributeUseDataTypeDescriptionContains all attributes of the Base Node ClassIsAbstractMandatoryBooleanIndicates whether the DataType is abstract. An abstract DataType can be used in the DataType Attribute. However, concrete values must be of a concrete DataTypeView
A View is used to restrict the number of visible Nodes and References in a large Address Space. By using Views servers can organize their Address Space and provide views on it tailored to specific tasks or use cases.
The following attributes are specific for the View node class:
AttributeUseDataTypeDescriptionContains all attributes of the Base Node ClassContainsNoLoopsMandatoryBooleanThis Attributes indicates whether the Nodes contained in the View do span a nonlooping hierarchy when following hierarchical ReferencesEventNotifierMandatoryByteThis Attribute represents a bit mask that identifies whether the View can be used to subscribe to Events and whether the history of Events is accessible and changeableThe next chapter describes the OPC UA NodeId Concepts.

## Slide 58: Configuration with OPC UA NodeID
In OPC UA, every entity in the address space is a node. To uniquely identify a Node, each node has a NodeId, which is always composed of three elements: NamespaceIndex, IdentifierType, Identifier.
There is an XML notation defined by the OPC UA XML Schema which represents a fully qualified NodeId. The format of the string is:ns=<namespaceIndex>;<identifiertype>=<identifier>
Flag | Identifier Type
i | NUMERIC (UInteger)
s | STRING (String)
g | GUID (Guid)
b | OPAQUE (ByteString)
Examples:
ns=2;s=MyTemperature
namespace index 2, string identifier
i=2045
namespace index 0, numeric identifier
ns=1;g=09087e75-8e5e-499b-954f-f2a9603db28a
namespace index 1, GUID identifier
ns=1;b=M/RbKBsRVkePCePcx24oRA=='
namespace index 1, Opaque/ByteString identifier
Notes: Difference to “Classic” OPC DA
In the old days the classic DA Server have used simple “string”-Identifiers. The so called “ItemID” was a fully qualified name that was unique throughout the whole server (there was only one “namespace”). Furthermore, the classic DA Servers had only capabilities for a simple hierarchy, i.e. a tree-like structure with branches and leaves. Hence, many vendors have used the full folder hierarchy to create unique ItemIDs (e.g. “Folder1.Folder2.Folder3.MyTemperature”). This lead to massive redundant strings, wasting memory and slowing down performance when looking up or searching for individual Items. With OPC UA, this concept has been abandoned.
OPC UA NodeIds
In OPC UA, every entity in the address space is a node. To uniquely identify a Node, each node has a NodeId, which is always composed of three elements:
NamespaceIndexThe index an OPC UA server uses for a namespace URI. The namespace URI identifies the naming authority defining the identifiers of NodeIds, e.g. the OPC Foundation, other standard bodies and consortia, the underlying system, the local server. They are stored in the so-called namespace array (also referred to as namespace table). Namespace indexes are numeric values used to identify namespaces to optimize transfer and processing. The namespace index is the index of the namespace URI in the namespace array.IdentifierTypeThe format and data type of the identifier. It can be a numeric value, a string, a globally unique identifier (GUID), or an opaque value (a namespace specific format in a ByteString). Which type is preferred depends on the use case. If it is important to save memory or bandwidth, it makes sense to use numeric NodeIds which are smaller and faster to resolve. The OPC UA namespace as defined by the OPC Foundation uses numeric NodeIds. System-wide and globally unique identifiers allow clients to track Nodes, e.g. work orders, moving between OPC UA servers as they progress through the system.IdentifierThe identifier for a node in the address space of an OPC UA server.The following image shows examples for NodeIds having different identifier types.
Examples for different types of NodeIds
XML Notation
There is an XML notation defined by the OPC UA XML Schema which represents a fully qualified NodeId. The format of the string is:
ns=<namespaceIndex>;<identifiertype>=<identifier>
with the fields
<namespace index>The namespace index formatted as a base 10 number. If the index is 0, then the entire “ns=0;” clause is omitted.<identifier type>A flag that specifies the identifier type. The flag has the following values:
FlagIdentifier TypeiNUMERIC (UInteger)sSTRING (String)gGUID (Guid)bOPAQUE (ByteString)<identifier>The identifier encoded as string. The identifier is formatted using the XML data type mapping for the identifier type. Note that the identifier may contain any non-null UTF8 character including whitespace.Examples:
ns=2;s=MyTemperaturenamespace index 2, string identifieri=2045namespace index 0, numeric identifierns=1;g=09087e75-8e5e-499b-954f-f2a9603db28anamespace index 1, GUID identifierns=1;b=M/RbKBsRVkePCePcx24oRA=='namespace index 1, Opaque/ByteString identifierThe identifier part of a NodeId uniquely identifies a node within a namespace, but it is possible that the same identifier is used in different namespaces for different nodes. Hence only the namespace plus the identifier forms a fully qualified identifier (see figure below). This means if a client requests a node, e.g. in a read service, it not only needs the identifier, but also the namespace the node belongs to.
Nodes with the same identifier in different namespaces
In OPC UA service calls the namespace index is used instead of the longer namespace URI in NodeIds. The Client needs to take care of the correct mapping from namespace URI to namespace index. Servers are not allowed to change the namespace index for a specific namespace URI or delete entries from the namespace table as long as an active session exist, so that clients can cache the namespace table for a specific session. But a Server may change namespace indexes and remove entries from the namespace table if no Client is connected or if the server is restarted. For this reason, a Client should not persist the namespace index without storing the namespace URI as well, because a namespace URI represented by index “2” during one session could be represented by index “5” during the next session. Thus, when having established a session with a Server, a Client should always read the Server’s namespace table and update namespace indexes before calling services in which NodeIds are involved.
The following figure shows a typical procedure a Client follows when reading atrributes of a node. In this example, the client wants to read the Node represented by the identifier “MyTemperature” which belongs to the namespace identified by the URI “urn:MyCompany:UaServer:Model2”. The client stores an own namespace table containing the URIs it is interested in to build up fully qualified NodeIds, but doesn’t yet know the corresponding namespace index in the Server namespace table. For being able to access the correct Node, the client has to read the Server namespace table first. The namespace URI “urn:MyCompany:UaServer:Model2” is represented by namespace index “3” on the Server. Now the client is able to update the namespace indexes in its own namespace table and the NodeId it wants to access (in our example this means replacing index “2” with index “3”) and has all information that is needed to access the correct node, in our example “ns=3;s=MyTemperature” in XML notation. As it is allowed that the namespace identified by the URI “urn:MyCompany:UaServer:Model1” also contains a Node having the identifier “MyTemperature”, the client may not even notice that it accessed the wrong node when reading “ns=2;s=MyTemperature”.
Reading and storing the namespace table
The next chapter describes the OPC UA Subscription Concept.

## Slide 59: OPC UA Configuration Hands-On Exercise 4
Hands-on
Asset configuration OPC UA

## Slide 60: MindSphere Launchpad Summary
What is OPC UA and why is it important for MindSphere communication?
OPC UA is a M2M communication protocol for industrial automation developed by the OPC Foundation. It is an open, cross-platform, Service-oriented architecture with robust security.
By being able to use OPC UA, MindSphere becomes an open source platform to connect 3rd party assets.

## Slide 61
MindSphere Assets
Configuration of MindConnect FB
2018

## Slide 62: MindSphere Assets Learning Goals
Configure MindConnect FB in TIA-Portal
Onboard MindConnect FB to MindSphere
What ist the MindConnect FB
And
How is the MindConnect FB onboarded to MindSphere?
Notes: Go through the agenda of today’s training with explanation for each item
MSPH Ecosystem -> How does it look like & what parts do exist in the MSPH ecosystem?
MSPH Scalable Portfolio -> What does MSPH currently offer (e.g. infrastructure, APIs, apps)?
IT security -> How do we make sure your data is safe and no one has unauthorized access to your data?
Demonstration/Hands-On -> Probably most interesting part as we onboard a device to MSPH and let actually a training participant connect the device with MSPH
Use Cases - MindApps & Connectivity -> For which use cases can MindSphere be used or is being used already? What are the benefits for our customers?
MSPH Pricing Model -> Chapter to illustrate the costs which will be something most participants want to know
MSPH forums and networks -> How do I as a customer get in touch, e.g. to get help or answers to general questions?

## Slide 63: MindSphere Connectivity Suite MindConnect FB 1500*
MindConnect FB is a TIA Portal STEP7 Library to extend the functionality of the S7-1500 PLC. It supports encrypted transmission of PLC data to MindSphere through a secure internet connection, to enable cloud-based applications and services.
  Fast and easy connectivity of industrial machines and automation systems to MindSphere
  Simple configuration and commissioning - Configure your data model in STEP 7 (TIA Portal V14)
  No additional hardware needed
  Unencrypted onsite (local) traffic which allows local package inspection
  Comprehensive security concept in accordance with applicable industry standards
  Local data buffering possible
  S7-1500 acts as gateway into field-level which allows access to various data sources
  Data reading cycle: Up to 110 data points per second can be configured in TIA Portal (the exact amount of data points depends on each controller)
  Data transfer cycle: Every 10 seconds
Description
Benefits
Supporting Protocols
Performance
* Compatible with S7-1511 to S7-1518 with firmware 2.0 or higher
Integrated Gateway
2

## Slide 64: MindConnect FB
Sample of data configuration of a motor with its data points “temperature”, “voltage” and “power” of the aspect “PowerConsumption” in MindSphere and STEP7 (TIA Portal) professional.
Configuring steps:
Configure Asset in MindSphere
Configure MindConnect FB in TIA Portal
Start onboarding and data sending
To use the MindConnect FB, TIA Portal V14 and S7-1500 V2.x is needed!

## Slide 65: MindConnect FB Configuration Hands-On Exercise 6
Onboard MindConnect FB from TIA Portal
Hands-on
Pc with internet access and valid credentials for MindSphere is available
Create MindConnect FB as asset in MindSphere and prepare onboarding
information to configure MindConnect FB in S7-1500

## Slide 66: Configuration of MindConnect FB Summary
What are the differences between MindConnect Nano/Iot2040 and MindConnect FB?
MindConnect FB is no physical connect element, it is a function block for TIA-Portal which you can directly integrate in your S7-1500 to connect to MindSphere without a MindConnect Nano or MindConnect IoT2040.
.

## Slide 67
MindConnect IoT Extension & MindConnect Integration

## Slide 68: MindConnect IoT Extension & MindConnect Integration Learning Goals
Get familiar with the two new MindConnect Elements
Get familiar with the user interface
What ist MindConnect IoT Extension &
MindConnect Integration?
Notes: Go through the agenda of today’s training with explanation for each item
MSPH Ecosystem -> How does it look like & what parts do exist in the MSPH ecosystem?
MSPH Scalable Portfolio -> What does MSPH currently offer (e.g. infrastructure, APIs, apps)?
IT security -> How do we make sure your data is safe and no one has unauthorized access to your data?
Demonstration/Hands-On -> Probably most interesting part as we onboard a device to MSPH and let actually a training participant connect the device with MSPH
Use Cases - MindApps & Connectivity -> For which use cases can MindSphere be used or is being used already? What are the benefits for our customers?
MSPH Pricing Model -> Chapter to illustrate the costs which will be something most participants want to know
MSPH forums and networks -> How do I as a customer get in touch, e.g. to get help or answers to general questions?

## Slide 69: Connectivity Services Offering Overview – connectivity for MindSphere 3.0
Integrate cloud-based and on-premise based Enterprise & Data Systems to MindSphere and enrich your data model with an extensive range of additional context data
Offering in V3.0
Added Value
MindConnect Integration
MindConnect LIB
MindConnect API
MindConnect Nano
Get access to a restful API to develop your own agents and bring your data into MindSphere
Use a C-based library as an application example to develop your own agents and bring your data into MindSphere
Get an out-of-the-box connectivity element to establish your data connection into MindSphere within 15 minutes without development effort
Extend the range of IoT devices that can easily be connected to MindSphere (e.g. Raspberry Pi, SIGFOX, Dell Edge GW) or use further adaptable software-agents (e.g. MQTT, Java, C++ agents) on your custom device
MindConnect IoT Extension
new
new
new
improved
improved

## Slide 70
Cloud
On Premise
2017
21 days
61 days
61 days
62 days
62 days
60 days
Architecture MindConnect Integration & IoT Extension
Usecase 1: Timeseries Upload
MindSphere Core Platform
MindConnect Integration
MSPH Adapter
MCI Agent
Cloud Systems (e.g. AWS S3)
MindConnect IoT Extension
Cumolocity Agent
IoT Devices supported by Cumolocity
MCI Adapter
MCI APP
IT/OT Systems (e.g SAP)
Developed by Software AG
Operated by Software AG

## Slide 71
2017
21 days
61 days
61 days
62 days
62 days
60 days
Big Picture Connectivity
MindSphere Core Platform
MindConnect Integration
On Premise
MindConnect IoT Extension
3rd Party IoT Devices & sensors
MindConnect API
LIB
FB*
Nano
3rd Party
IT & OT Systems
Cloud
3rd Party Cloud Services
*ownsership transferred to DF FA SUP

## Slide 72
2017
21 days
61 days
61 days
62 days
62 days
60 days
Architecture MindConnect Integration & IoT Extension
Whitelable Overview
MindSphere Core Platform
MindConnect Integration
On Premise
MindConnect IoT Extension
3rd Party IoT Devices & sensors
Agent SDKs
Agent references
Cumulocity certified devices
3rd Party
IT & OT Systems
Cloud
3rd Party Cloud Services
Components
Integration Server
Designer
Installer/ Updater
MindSphere branded
Cloud Environment
Software AG branded
MindSphere branded
3rd party branded
Partner branded
Field Level

## Slide 73
2017
21 days
61 days
61 days
62 days
62 days
60 days
Architecture MindConnect Integration & IoT Extension
User Journey Overview
MindSphere Core Platform
MindConnect Integration
MindConnect IoT Extension
MindConnect IoT Extension
Rasperry Pie Sensor
1
2
3
4
5
6
7
8
9
0
1
2
3
5
6
7
8
9
0
1
2
3
4
5
6
7
8
9
0
1
2
3
4
5
6
7
8
9
0
1
2
3
4
5
6
7
8
9
0
1
2
3
4
5
6
7
8
9
0
1
2
3
4
5
6
7
8
9
0
4
1
1
2
3
5
6
7
8
9
0
4
1
2
3
4
5
6
7
8
9
0
1
2
3
4
5
6
7
8
9
0
1
2
3
4
5
6
7
8
9
0
1
2
3
4
5
6
7
8
9
0
2
3

## Slide 74
2017
21 days
61 days
61 days
62 days
62 days
60 days
MindConnect Integration & IoT Extension
Whitelabeling Aspects
The complete customer journey on cloud side is white labeled
  Allow seamless MindSphere experience between all cloud services
Everything needed on field level is branded as Software AG/Cumulocity/3rd party
  Cumulocity is a huge, established ecosystem including SDKs, forums and communities which we need to leverage
  Agent & on premise adapter development environment is very dynamic und would cause continuous white labeling efforts
  Software AG is domain expert in on-premise integration scenarios
  To get access to installer, designer, on premise adapters, SDKs and agent references for field level the customer leaves the MindSphere branded environment and uses Software AG/ Cumulocity branded content.



## Slide 75: Connectivity MindConnect IoT Extension
MindConnect IoT Extension1) Expand MindSphere connectivity to all machines across the production floor
SW Agents: MQTT Agent, Java Agent, C++ Agent
Agent Development: REST API
Field protocols: HTTP/HTTPS, TCP, VNC, MQTT / MQTT+TLS, REST, SmartRest 1.0 / 2.0, OPC-UA, Modbus/RTU, Modbus/TCP, CAN bus, MMC, SPI, I2C, McASP, device specific protocols
Devices: Adeunis LoRAWAN, BeagleBone Black, Cinterion Java Modules, CloudGate, Dell Edge Gateway, INSYS Smart Devices – INSYS OS, INSYS Smart Devices – icom OS, Janz Tec emPC A/RPI, Libelium-Mesehlium, Mbed u-blox C027, Meitrack, Netcomm, PCUA Java Gateway, OWA3x, QuecLink, RaspberryPi, Red Lion RAM, SMARTBox, Robustel, SIGFOX, SMARTBox IO, SMARTBox Mini, TC3G, Telic, TinkerForge, Tixi
1) Limited to small files and time series values

## Slide 76: Connectivity MindConnect Integration
MindConnect Integration1) Establish connectivity with existing databases and enterprise systems to open new avenues of analysis
Cloud connectors: FTP(S), SOAP, REST, OData 2.0, OData 4.0, Alfabet, Cumulocity, Apps, BigQuery, Calendar, Cloud Storage, Contacts, Drive, Cloud Pub/Sub, Sheets,S3, SNS, SQS, Apache Solr, AvaTax, Concur, Coupa, Magento, Marketo, Microsoft Dynamics, NetSuite, SAP cloud, SAP Hana Marketing Cloud, Salesforce, Salesforce CRM, ServiceNow, Slack, StrikeIron, SuccesFactors, SugarCRM, Zendesk
On premise connectors: Ariba, OnRamp, LotusNotes, OFTP, Oracle, PeopleSoft, Remedy, SAP, SAP XI, Siebel, AS/400, JavaBeans, JDBC, Apache HIVE, MongoDB, Cassandra, HDFS, Apache Impala, Apache WebSphereMQ, Tuxedo, MSMQ, Apache Kafka
1) Limited to small files and time series values

## Slide 77: MindConnect IoT Extension & MindConnect Integration Hands-On Exercise 7
MindConnect IoT Extension and MindConnect Integration
https://tepusr.eu1.mindsphere.io
https://demoprm.mcintegration.eu-central-preview.mindsphere.io/integration/login#/login
https://demoprm.mciotextension.eu-central.mindsphere.io/apps/cockpit/index.html#/

## Slide 78: MindConnect IoT Extension & MindConnect Integration Summary
MindConnect IoT Extension Expand MindSphere connectivity to all machines across the production floor
MindConnect Integration Establish connectivity with existing databases and enterprise systems to open new avenues of analysis

## Slide 79
MindConnect
Device Training
Summary & Feedback
2018

## Slide 80: MindSphere Summary & Feedback Learning Goals
Where do I find relevant information about MindSphere and MindSphere products?
Ecosystem Community
SIOS
Support Contacts

## Slide 81: MindSphere Forums & Network
  SIOS: Siemens Industry Online Support
Provide the last technical documents from Fact Sheets to Quick Start Guides and Customer Documents
https://support.industry.siemens.com

## Slide 82: MindSphere Connect to Us
Website | www.mindsphere.io
MindSphere Community | https://community.plm.automation.siemens.com/t5/MindSphere/ct-p/MindSphere
MindSphere General | contact@mindsphere.io
MindSphere Support Team | Call Center: +49 (0)911 895 7 272 (Germany) Online Support: http://www.siemens.com/automation/service&support Support Request: http://www.siemens.com/automation/support-request
MindSphere Academy | training@mindsphere.io

## Slide 83: Forums & Network Summary
Where do I find relevant information about MindSphere and MindSphere products?
A: MindSphere offers a wide range of opportunities to network within the ecosystem and collect informations.

## Slide 84
Thank you.